## CALCULATIONS
Segment | Length(m) | OD(mm) | Thickness(mm) | ID (m) | Mass Flow (Kg/s) | Density (kg/m³) | Velocity (m/s) | Reynolds No. | Friction Factor | Total K | Elevation Change (m) | Major Loss (pa) | Minor Loss (pa) | Elevation Loss (pa) | Segment Pressure Loss (pa) | Segment Pressure Loss (bar) | Inlet Pressure (bar) | Outlet Pressure (bar)
S1 | 1.3 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 19.5937 | 0 | 0 | 19.5937 | 0.00019594 | 10.7873 | 10.7871
S2 | 1.1 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.3 | 0 | 16.5793 | 58.7429 | 0 | 75.3221 | 0.00075322 | 10.7871 | 10.7864
S3 | 2 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 30.1441 | 0 | 0 | 30.1441 | 0.00030144 | 10.7864 | 10.7861
S4 | 3 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.6 | 0 | 45.2162 | 117.4857 | 0 | 162.7019 | 0.001627 | 10.7861 | 10.7844
S5 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.15 | 0 | 75.3603 | 29.3714 | 0 | 104.7318 | 0.0010473 | 10.7844 | 10.7834
S6 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.55 | 0 | 75.3603 | 107.6952 | 0 | 183.0556 | 0.0018306 | 10.7834 | 10.7816
S7 | 4 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.3 | 0 | 60.2883 | 58.7429 | 0 | 119.0311 | 0.0011903 | 10.7816 | 10.7804
S8 | 3.06 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.3 | 0 | 46.1205 | 58.7429 | 0 | 104.8634 | 0.0010486 | 10.7804 | 10.7793
S9 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.4 | 0 | 75.3603 | 78.3238 | 0 | 153.6841 | 0.0015368 | 10.7793 | 10.7778
S10 | 4.5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 1.1 | 0 | 67.8243 | 215.3905 | 0 | 283.2148 | 0.0028321 | 10.7778 | 10.775
S11 | 1.1 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.3 | 0 | 16.5793 | 58.7429 | 0 | 75.3221 | 0.00075322 | 10.775 | 10.7742
S12 | 3.6 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.15 | 0 | 54.2594 | 29.3714 | 0 | 83.6309 | 0.00083631 | 10.7742 | 10.7734
S13 | 3.4 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.6 | 0 | 51.245 | 117.4857 | 0 | 168.7307 | 0.0016873 | 10.7734 | 10.7717
S14 | 3.6 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.55 | 0 | 54.2594 | 107.6952 | 0 | 161.9547 | 0.0016195 | 10.7717 | 10.7701
S15 | 1.15 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 17.3329 | 0 | 0 | 17.3329 | 0.00017333 | 10.7701 | 10.7699
S16 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.3 | 0 | 75.3603 | 58.7429 | 0 | 134.1032 | 0.001341 | 10.7699 | 10.7685
S17 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.4 | 0 | 75.3603 | 78.3238 | 0 | 153.6841 | 0.0015368 | 10.7685 | 10.767
S18 | 5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0.15 | 0 | 75.3603 | 29.3714 | 0 | 104.7318 | 0.0010473 | 10.767 | 10.766
S19 | 3.5 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 52.7522 | 0 | 0 | 52.7522 | 0.00052752 | 10.766 | 10.7654
S20 | 1 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 15.0721 | 0 | 0 | 15.0721 | 0.00015072 | 10.7654 | 10.7653
S21 | 3 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 45.2162 | 0 | 0 | 45.2162 | 0.00045216 | 10.7653 | 10.7648
S22 | 6 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 90.4324 | 0 | 0 | 90.4324 | 0.00090432 | 10.7648 | 10.7639
S23 | 1.95 | 219.1 | 6.35 | 0.2064 | 1.3889 | 4.4 | 9.4342 | 428388.628 | 0.015887 | 0 | 0 | 29.3905 | 0 | 0 | 29.3905 | 0.00029391 | 10.7639 | 10.7636

## SETTINGS
Parameter | Value | Unit
Start pressure | 11 | kg/cm²
Temperature | 320 | °C
Mass flow | 5 | tph
Mass flow | 1.3889 | Kg/s
Atmospheric Pressure | 1.0132 | bar
Start pressure | 11.8006 | bar
Gravity | 9.8066 | m/s²
Steam Properties
Parameter | Value | Unit
Main pipe OD | 219.1 | mm
Wall Thickness | 6.35 | mm
Main pipe ID | 206.4 | mm
Main pipe ID | 0.2064 | mm
Pipe Roughness | 4.5e-05 | mm
Steam density | 4.4 | kg/m³
Steam velocity | 2e-05 | pa.s
Fitting Settings
Component | Count | K per item | Total K
90° elbow |  | 0
Gate valve
Globe valve
Tee-through
Tee-branch
Reducer
Total K |  |  | 0